## Sheet1
MANIFOLD AUTHORIZATION POLICY
PURPOSE: |  |  | To regulate manifold meter placement in order to minimize maintenance issues and pressure complaints.
SCOPE: |  |  | This document recounts the site conditions required before a manifold metering system can be considered and outlines the review procedure to validate the request.
RESPONSIBILITY & AUTHORITY: |  |  | Charlotte Water Engineer shall review each submitted site plan for compliance and confirm manifold systems adhere to all design standards.
QUALIFYING CRITERIA:
The uncontrolled use of manifold meters can present some maintenance challenges and cause confusion surrounding private line ownership and levels of service provided by CLTWater, but in certain situations provide a practical alternative utilizing dedicated meters. Advantages include:
1. Eliminates multiple service taps on a short segment of a water main, preserving the integrity of the pipe and reducing expensive pavement cuts.
2. Replaces ‘gang meters’ which requires multiple meter boxes along the road, multiple connections onto the water main, and multiple street crossings.
3. Allows the applicant to pay capacity fees for individual 5/8” meters versus capacity fees required for a master meter.
4. Eliminates sub-metering issues for small infill development projects, thus satisfies requests of the private development community.
5. Provide individual metering for small townhome and condominimum projects, small single development projects with private streets, lots without direct access to public water.
To manage and restrict manifold system requests, a set of guidelines have been established:
1. Each 2-inch Manifold meter connection will provide water service to no more than 20 residences or the equivalent of 20 residential units at a single development. This condition is based on Section .0900 NC Distribution Systems.
2. Single family lots with limited public road frontage/access to public water may be considered on a case by case basis by the CLT Water Engineer.
3. If manifold vault and/or private service lines traverse across privately owned parcels, private utility easements are required for the private service lines. A CLT Water public water easement will be required for vaults when located within individual property owners parcels. A public water main easement may not be required for vaults when located within common open space maintained by HOA's, COA's or other, as determined by CLT Water.
4. Manifold Meter Vault shall be placed at practical locations, in/or adjacent to the public road (ROW), in the vicinity of the buildings they intend to serve and will be subject to Charlotte Water Review and Approval.
5. Flow and head loss calculations shall be provided for the worst case building unit. Site Engineer must provide calculations verifying that a minimum of 20 psi will be provided to the highest fixture in the unit top floor of the furthest and/or highest building from the manifold system. These calculations will be based on the static pressure conditions of the site in question and the Operational Low Tank Level for the Pressure Zone serving the site, as provided by Charlotte Water and defined as follows:
| PRESSURE ZONES |  |  | OPERATIONAL LOW TANK LEVEL*
|  | 882 |  |  |  | 847
|  | 960 |  |  |  | 922
|  | 978 |  |  |  | 939
*=ELEV. ABOVE SEA LEVEL
**Manifold water services shall not be permitted in the Pineville Pressure Zone
8. Design assumptions and calculations may be subject to review and approval by Charlotte Water. The following information shall be provided:
METER ELEVATION:
ADDRESS/UNIT No. AND STREET
FIRST FLOOR ELEVATION:
NUMBER OF FLOORS:
HIGHEST FIXTURE ELEVATION:
PIPE MATERIAL/CLASSIFICATION(PRESSURE/THICKNESS):
PIPE INSIDE AND OUTSIDE DIAMETER:
HAZEN WILLIAMS FRICTION COEFFICIENT (copper=130,hdpe=140):
FLOW RATE(≥8 ≤10 GPM):
LENGTH OF PIPE FROM METER TO UNIT(ft):
9. The following head loss/pressure loss conditions shall be included in the calculations:
AT A MIN FLOW RATE OF 8 GPM
PRESSURE LOSS(PSI)
WATER METER (Use 1.0) | [5 empty] | 1
3/4" SERVICE ASSEMBLY IN VAULT (Use 2.5) | [5 empty] | 2.5
2" SERVICE ASSEMBLY IN VAULT (Use 1.0) | [5 empty] | 1
2" SERVICE LINE (TAP TO MANIFOLD) LENGTH < 60 FT "SHORT SIDE" USE 0.7 OR
LENGTH > 60 FT "LONG SIDE" USE 1.6
TOTAL APPLICABLE PRESSURE LOSS(PSI)* | [5 empty] | 4.5
HAZEN-WILLIAMS COEFFICEINT (PRESSURE LOSS) CALCULATOR
ACTUAL PIPE INSIDE DIAMETER (ID):
FRICTION COEFFICIENT:
FLOW RATE (Use 10 gpm): |  |  |  |  | 10
LENGTH OF PIPE, FT (MANIFOLD TO UNIT):
OUTPUT:
PRESSURE LOSS (FT):
PRESSURE LOSS (PSI):
TYPE K COPPER 0.75"(ID) |  |  | 0.745"
HDPE SDR9 0.75" CTS (ID) |  |  | 0.669"
TYPE K COPPER 1.0"(ID) |  |  | 0.995"
HDPE SDR9 1.0" CTS (ID) |  |  | 0.875"
HW COEFFICIENT(COPPER) |  |  | 130
HW COEFFICIENT(HDPE) |  |  | 140
(OPERATIONAL LOW TANK LEVEL) - (HIGHEST FIXTURE ELEVATION) X (0.434) = STATIC PRESSURE AT LOCATION
|  |  |  | 0 |  |  | 0 | PSI
STATIC PRESSURE AT LOCATION (PSI) - TOTAL PRESSURE LOSS (PSI) | [8 empty] | PSI
I hereby acknowledge that I have read this Manifold Meter Policy and I have provided the calculations verifying that, given the specific site criteria, a minimum of 20PSI will be provided to the highest fixture at the furthest unit within the proposed site.
ENGINEER'S SIGNATURE & SEAL: | [5 empty] | DATE: